# METAL COLUMN LOUDSPEAKER

# MCS80/TC

### Architects & Engineers Specification

The unit shall be the PENTON model MCS80/TC or equal and approved. The loudspeaker enclosure shall be constructed in aluminium with a separate grille both epoxy powder coated to match. The unit will be supplied with “L” shaped mounting brackets.  The loudspeaker assembly shall comprise of 8 x 75mm diameter, coated drive units and a horn type tweeter. To minimise visual impact the speaker dimensions should not exceed 970x98x90mm (H x W x D).

An 80watt / 100 volt line, factory fitted transformer shall provide 3dB power taps via a recessed selector switch situated at the base of the unit.

Cable entry will be via a single cable entry located at the rear of the cabinet.

The loudspeaker shall have a tailored dispersion. The cones shall be damped, high compliance units with a smooth extended frequency response.

The MCS80/TC will be suitable for voice alarm applications and will be supplied with ceramic terminals to take 2 x 2.5mm² conductors and a thermal fuse rated at 150˚. A 4-core fire rated cable tail should be added to ensure full compliance or the addition of a second cable entry to allow “loop in, loop out” termination.

This loudspeaker must be compliant to BS5839 part 8 & EN60849.

### Rated power 	80w

### Tappings 100v line	80/40/20/10w
Effective frequency range               	180 ~18Khz

### SPL @ 1w/m (test signal 100Hz~10kHz)               	96dB                                    
Dispersion at 1k/2kHz                                                	180/140 (Horizontal)
                                                                                  	70/ 45 (Vertical)
Axial Q Factor at 1k/2kHz                                    	4.2/6.8

### Colour                                                                       	White

All units to be tested in accordance with BSEN60268-5

Penton UK Ltd, Unit 2, Teville Industrials, Dominion Way, Worthing, West Sussex BN14 8NW

Tel: 01903 215315 Fax: 01903 215415 E-Mail: sales@pentonuk.co.uk Web: www.penton.org