WEATHERPROOF 
METAL HORN LOUDSPEAKER

MHS20/TC

# Architects & Engineers Specification

The unit shall be the PENTON model MHS20/TC or equal and approved. The horn enclosure shall be constructed of a weather-resistant, LM4 aluminium die-cast housing incorporating a rear chamber. The unit will be mounted via a lockable, stainless steel “U” bracket and fixings.  The loudspeaker diaphragm shall comprise of a high density phenolic resin type capable of withstanding water and dust ingress up to a minimum IP65 Norms housed in a flared chamber,

297mm long x 217mm diameter.

A 20watt / 100 volt line, factory fitted transformer shall provide 3dB power taps via a selector switch mounted in the rear chamber of the loudspeaker.  Cable entry shall be via 2 x 16mm cable entries, 1 x cable gland and 1 x blanking plug will be mounted on a removable rear cover.

The loudspeaker shall have a controlled dispersion. The cone shall be high a compliance unit with a smooth extended frequency response.

The MHS20/TC will be suitable for voice alarm applications and will be supplied with ceramic terminals to take 2 x 2.5mm² conductors and a thermal fuse rated at 150˚. A 4-core fire rated cable tail should be added to ensure full compliance or the addition of a second cable entry to allow “loop in, loop out” termination.

This loudspeaker must be compliant to BS5839 part 8 & EN60849.

### Rated power 	20w

### Tappings 100v line	20/10/5/2.5/1.25w
Effective frequency range               	300 ~16.5Khz

### SPL @ 1w/m (test signal 100Hz~10kHz)               	101dB                                    
Dispersion at 1k/2kHz                                                 100/98
Axial Q Factor at 1k/2kHz                                    	4.7/12.5

### Colour                                                                        Grey

All units to be tested in accordance with BSEN60268-5

Penton UK Ltd, Unit 2, Teville Industrials, Dominion Way, Worthing, West Sussex BN14 8NW

Tel: 01903 215315 Fax: 01903 215415 E-Mail: sales@pentonuk.co.uk Web: www.penton.org