VANDALPROOF SQUARE,

FLUSH MOUNT,
 METAL CABINET LOUDSPEAKER

WITH LED STROBE

SENTRY6/TBBCL

# Architects & Engineers Specification

SPEAKER

This unit shall be the PENTON model SENTRYT6/TBBCL or equal and approved. The assembly shall comprise of a 140mm diameter dual coned loudspeaker and shall be fitted with a 6 watt/100 volt line factory fitted transformer with the power taps clearly marked on the assembly.

The flush mount loudspeaker cabinet shall be constructed as a two-part unit to enable first and second fix installation. The back box will be manufactured in galvanised steel. Cable entry will be via 2 x 20mm cable entries located on the side and rear of the cabinet. The speaker with integrated chassis and grille will be constructed in steel and epoxy powder coated.

Loudspeaker shall have a wide-angle dispersion. The cone shall be a damped, high compliance type with a smooth extended frequency response.

The SENTRY6/TBBCL will be suitable for voice alarm applications and will be supplied with ceramic terminals able to take up to 2 x 2.5mm² conductors per terminal and a thermal fuse rated at 150˚.

This loudspeaker must be compliant to BS5839 part 8 & EN60849.

BEACON

The SENTRYT6/TBBCL shall be fitted with a high intensity, low profile beacon mounted in the centre of the speaker grill for maximum visibility. The beacon will be fitted with a RED LED and a clear lens.

### Rated power                                                          6w

### Tappings 100v line                                                6/3/1.5/0.75/0.25w
Effective frequency range                                   180 ~17 KHz

### SPL @ 1w/m (test signal 100Hz~10 kHz)              92dB
Dispersion at 1 k/2kHz                                         170/120
Axial Q Factor at 1 k/2kHz                                  2.3/4.9

### Colour                                                                   White

### Voltage / current LED strobe                              24VDC Polarized, 6.3mA (0.15w)
Flash rate of strobe per minute                          55 – 60

Intensity of Strobe in Lux @ 75mm                      57

All units to be tested in accordance with BSEN60268-5

Penton UK Ltd, Unit 2, Teville Industrials, Dominion Way, Worthing, West Sussex BN14 8NW

Tel: 01903 215315 Fax: 01903 215415 E-Mail: sales@pentonuk.co.uk Web: www.penton.org